## PREAMBLE TO SOR
DOCUMENT NO. (PA01)
E-Tender No.
PREAMBLE TO PRICE SCHEDULE
1 | Bidders are required to mention "Increase" or "Decrease" and quote percentage in figures as well as in words in the requisite cells by whcih total estimated price shall be increased or decreased along with loading of GST quoted in summery sheet to arrive at the bidder evalated price. The ranking of bidders(L1,L2....) shall be determined by the bidder quoted price(arrived after applying quoted percentage increase or decrease on total estimted price in accending order).
2 | Bidder has to mention the applicable GST in the summary sheet.
3 | Bidder has to upload the summary sheet giving percentage of " Increase" or "Decrease"along with SOR in the Price Bid folder.
3 | Details of delivery points as per project site location.
4 | As per Clause 171 of GST Act, it is mandatory to pass on the benefit due to reduction in rate of tax or from input tax credit to the consumer by way of commensurate reduction in prices. The Bidder may note the above and quote their prices accordingly.
5 | Bidder confirms that he has noted the contents of the preamble to the price schedule, bid document, and quoted his percentage.
6 | Bidder confirms that he has noted the contents of the preamble to the price schedule, bid document, and quoted his percentage accordingly without any deviation.
BIDDER'S SIGNATURE:
COMPANY'S NAME:
SEAL:
NOTES: | Bidders (Indian) must submit this document No. (PA01) duly signed and stamped with both unpriced & priced offer.

## SUMMARY
SUMMARY OF SCHEDULE OF RATES- PART D LAYING TENDER FOR CONSTRUCTION OF STEEL PIPELINE AND ASSOCIATED FACILITIES ON CGD Connectivity TO M/s. Think Gas Macchiwara (Ludhiana) E-Tender ref : 8000017675
|  |  | Bidder's Name: | ...........................................
Part | Description | Total Estimated Cost (inclusive of all applicable taxes & duties & other levies [if any] payable by the Contractor under the Contract, or for any other cause except final GST) in Rupees | Quoted Variation
|  |  | "INCREASE" OR "DECREASE" (Refer note no 1 below) | Percentage In Figures (upto two decimal places) | Percentage In Words (upto two decimal places)
(1) | (2) | (3) | (4 a) | (4 b) | (4 c)
A | Refer Detailed SOR sheet attached herewith | 11002254.55
2 | Notes: Bidder's total price to be arrived by applying quoted %age increase/ decrease on total estimated cost given at col. No. 3 above.
3 | Applicable GST (CGST&SGST/UTGST or IGST) rate on Total price (in %)
4 | Service Accounting Codes (SAC) as per GST act [To be filled by bidder]
Notes:
1 | Under Column '4a', the bidder has to indicate clearly either "INCREASE" or "DECREASE" as applicable. In case the column is left blank, it will be consdered as "DECREASE" in terms of percentage.
2 | In case of discrepency between percentage in figures & words, percentage in words will prevail.
Seal & Siganture of Bidder
Name of Authorized signatory

## Total
GAIL (India) Limited | SUMMARY OF RATES
Project : Construction of Steel Pipeline and Associated Facilities on CGD Connectivity to M/s Think Gas Macchiwara(Ludhiana)
E-TENDER NO. 8000017675
Sl. | Section | Description of work | In Figures
1 | A | Mainline Works | 4937330
2 | B | Mechanical Piping & Terminal Works | 1546281
3 | C | Civil & Structural Works | 2058680.5
4 | D | Cathodic Protection System Works | 599258.76
5 | E | Electrical Works | 771260
6 | F | Instrumentation Works | 386570
7 | G | Telecom Works | 702874.29
8 |  | Total Amount (inclusive of all applicable taxes & duties excluding GST) [1+2+3+4+5+6+7] | 11002254.55

## Sec-A
GAIL (India) Limited | SCHEDULE OF RATES (SOR): SECTION-A (MAIN LINE WORKS)
Project : Construction of Steel Pipeline and Associated Facilities on CGD Connectivity to M/s Think Gas Macchiwara(Ludhiana)
E-TENDER NO. 8000017675
Currency: INR
SOR Item No. | Description of Item | Unit | Qty. | ESTIMATED UNIT RATE INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT | ESTIMATED TOTAL AMOUNT INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT
|  | (1) | (2) | (3) | (4)
A00100 | PIPELINE LAYING / INSTALLATION (CARBON STEEL PIPES)
Receiving and taking over, as defined in the specifications, handing, loading, transportation and unloading of Owner-supplied 3-layer PE coated line pipes along with associated fittings and valves from Owner's designated stock-yard to Contractor's stock-yard / workshop / work-site including preliminary activities, preparation of drawings, wherever required for crossing, etc. including handling, stacking, stringing on the pipeline right-of-use / pipeline route alignment, carrying out inspection of Company-supplied materials, including line pipes, at the time of taking over, laying / installation of coated line pipes, associated fittings (IJ,barred tee etc) and accessories, including execution of all works, taking over, handling, including loading and unloading, arrangement of all additional land required for Contractor's storage, fabrication, access for construction, procurement and supply of all materials (except Owner-supplied materials), consumables, equipment, labour and other inputs, carrying out all temporary, ancillary, auxiliary works, ready for commissioning of pipeline, as per drawings, specifications, other provisions of Contract Document and instructions of Engineer-in-Charge (EIC), including, but not limited to, carrying out following works:
Survey required for entire pipeline route including surveying of detours for the detours required at the time of construction including marking the route map, alignment sheet, topographical sheet & other survey drawings, etc., preparation of AFC drawings showing survey details, and submit same to Owner for review.
Staking and installation of construction markers, clearing, fencing, grubbing, full filling all the requirements of various statutory / environment authorities to the entire satisfaction of concerned authorities, grading of work area. Shifting of all obstructions within the ROU / pipeline route alignment, viz. electrical lines / poles, telephone lines / poles, coordination with concerned authorities and obtaining permissions from these authorities.
Trenching to all depths by excavation in all types of soils except hard rock, chiselling or otherwise cutting different types of pavement, footpath, roads etc. as required and storing excavated soil, reusable materials at designated area as directed by Engineer in charge and to a width to accommodate the pipeline and optical fibre conduit as per the relevant standard / specification etc. [The minimum depth of the top of pipeline shall be 1.0m measured from top of pipeline coating to the top of undisturbed surface of the soil or as per Special Condition of Contract (SCC) / OSID - 141 OISD - 226]. Dewater of trenches if required as per site condition. Note : Extra payment on account of excavation in hard rock will be as per SOR item No. A00120 based on actual measurement for hard rock encountered as certified by the EIC.
Carrying out repairs of pipe defects / replacement in case of irreparable defects and repairs of defects of pipe coating not attributable to Owner including defects / damages occurring during transportation / handling.
Stringing of line pipes along ROU including providing straw / sand / soft soil bags, soft padding / sand padding.
Checking, cleaning, aligning, bending, cutting and bevelling (as required) of pipes for welding & field adjustments including pipe fittings, welding, carrying out non-destructive testing of welds as required including 100% radiography by X-Ray (in case of space constrant & small work by Gamma Ray on Owner's approval) as per specifications in piping of all types and thickness and providing all requisite equipment, labour, supervision, materials, films, consumables, all facilities & personnel to process, develop, examine and interpret radiographs & other tests as required, carrying out repairs of weld-joints found defective by EIC, carrying out re-radiography and other tests as required on repaired joints, etc. as mentioned in SCC and particular job specifications.
Installation of carrier line pipe at all crossings viz road, cartrack, pathway, drain, nallah & minor water crossings, etc. at designated depth by open cut (including laying of casing pipe) (except at HDD / Boring cased crossings which is covered separately elsewhere in this SOR).
Coating of all weld joints, long radius bends, etc.
Installation / lowering the pipeline in trench to required depth, placement of PE / PVC warning mat over the pipeline along the complete route, padding around pipeline with suitable approved soil including supply of padding material, PE / PVC warning mat, backfilling with available / borrowed earth, approved excavated material and /or other suitable soil by crowning.
Supply and installation of slope breakers, bank protection, wherever required and as directed by EIC.
Erection of isolation valves for pipelines inside the valve-pits and making provision to operate the valves at above ground level.
All tieing-in, including the tie-ins with adjacent section of the pipeline.
Lowering the pipelines in trench, providing required depth and backfilling over and around the pipeline with available, approved excavated material as per specification and / or other suitable soil approved by EIC.
Select soil for backfilling, if required, as per specification including supply of graded sand / rock / other types of soil in place of available excavated material and / or other suitable soil, including transportation of such special backfill material over all distances, complete.
Protective coating of 450 microns thick 2-component high built coal tar epoxy (applied with the help of minimum 3 coats) including supply of coating & other materials duly approved by Owner for all piping valves, fittings, structural steels, etc. for buried installation and inside the valve-pit.
Carrying out air cleaning, pigging, flushing, cleaning and hydrostatic testing of complete pipeline with required quantity of corrosion inhibitor including pre-testing of designated sections complete as per specification and approved by EIC to specified pressures indicated elsewhere and duration after stabilization as per specification, providing all equipment, pumps, fittings, instruments, dead weight tester, pressure recorder, thermocouples, etc., and services, supervision, labour, consumables, water including supply of corrosion inhibitor, air, etc. as required, locating of leaks and rectification of defect attributable to Contractor (rectification of defects in linepipe material not attributable to Contractor shall be paid separately as per other item of SOR), re-testing after rectification, dewatering after successful completion of hydrotesting of entire section and as approved by EIC, complete.
Swabbing of the complete pipeline section and the associated facilities being installed to the specified acceptance criteria, carrying out pre-commissioning works, providing assistance during the complete duration of commissioning operations for entire pipeline and making the entire pipeline system ready for commissioning including supply of all equipment, manpower, consumables (including pigs and Nitrogen required for maintaining Nitrogen column of minimum 5% of pipeline volume) materials for all temporary works and performing all associated works, complete as per the relevant specifications, other provisions of Contract Document and instructions of EIC.
Final clean-up of right-of-use and disposal of debris and surplus material to designated disposal areas and reinstalling the area to its earlier state as per satisfaction of concerned authority and as directed by EIC.
Preparation of as-built drawings, pipe-books (2 soft copy in AutoCad format in CD, 2 soft-copies in PDF format (in CD) and 4 hard-copies of pipe-book) All the works shall be executed in accordance with the provision of Contract including carrying out all temporary / ancillary / auxiliary works required for the performance of the works and all other acts, deeds, matters and things necessary to make the pipeline ready for precommisioning activities.
Line pipe laying & installation with radiography
Specified Size (NB)
A00101 | 100 (4"), diff. grades & thickness | Meter | 900 | 4353 | 3917700
Note: (1) This item shall be applicable for the underground steel main pipeline & underground tap-off points (i.e. including arrangement for making provision for tap-off except hot tapping and their hook-up) on existing / proposed steel main pipeline to Insulating Joint at proposed Receiving / Dispatch Station; (2) All crossings installed by HDD / jacking / boring shall be paid separately as per the rates quoted for the same elsewhere in the SOR.
A00130 | Supply and installation of Concrete Slab / HT sheeting for Protection of Pipeline against underground HT cables /over head HT lines as per drawing and specification attached with tender document | Running Meter | 3 | 4430 | 13290
A00300 | INSTALLATION OF CARRIER PIPE CROSSINGS BY HDD METHOD AT CROSSING WITHOUT CASING PIPE in all types of soils, soft rock/murram except hard rock
“Complete work of installation of carrier pipe at crossings (between the limits as defined in approved drawings. Drawing preparation and obtaining the approval on the same is included in the scope of Contractor) by HDD method for roads, nallahs, drains and canals, wherever required, in all types of soils, soft rock/ murram except hard rock, including "receiving and taking over" Owner-supplied 3-layer PE coated line pipes from Owner's designated place of issue / dump-site(s) and transportation to Contractor's stock-yard / workshop / work-site including all handling loading, unloading, aligning, etc. supply of all Contractor-supplied materials, including CS CONDUIT of size 150mm NB, 6.4mm thick. as per API - 5L Gr. B or equivalent , manpower, equipment, consumable, other resources and acquiring the required land for storage, fabrication, including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification, strapping of HDPE conduit or CS conduit subducted with HDPE conduit as the case may be with main pipeline for laying / blowing of OFC cables, pre-testing, etc. of complete string made for crossing access for Contractor, etc. and execution of, but not limited to, following works in accordance with the specifications and instructions of EIC, and as per all provisions of Contract Document.”
Pre-construction survey based on site-visit, carrying out all additional topographical, hydrological & geo-technical surveys as required for design & construction of crossing, collection of data (if reqd.) from concerned authority including design & detailed engineering and making of crossing drawings for getting their approval from concerned authority / EIC, getting work permit / NOC for crossings as well as utility crossings (if any) encountered during crossings prior to start the execution of work.
Drilling to required depth including maintenance of drill hole in all types of strata (in all types of soils, soft rock/ murram except hard rock,), all depth to accommodate the pipeline at all conditions encountered during crossing by approved HDD methods procedure for providing minimum cover specified in code / specification or as decided by concerned authority, whichever is more.
Backfilling of the ditch / trench including restoration and cleanup of area and all other works including cleaning, final hydrotesting, etc. alongwith mainline works (as mentioned in clause no. A00100 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of EIC and / or as directed by concerned authority.
A00310 | Installation of 4" NB 3LPE Coated Carbon Steel Pipeline by HDD | Meter | 36 | 16786 | 604296
Note: (1) The length mentioned in SOR is indicative for all the crossing to be done by HDD & locations shall be decided by GAIL / Consultant prior to start of job depending upon site-condition; (2) Payment for the length of final tied in carrier pipeline string with mainline laid by HDD are inclusive in this above item rate. No any separate payment shall be made under other clauses mentioned elsewhere.
A00600 | PERMANENT MARKERS
Supply, fabrication & installation of following types of permanent markers along the route including all associated civil works such as excavation in all types of soil, construction of pedestals & grouting with concrete, cleaning, supply & application of approved colour & quality of primer and paint, stencil letter cutting for numbers, direction, chainage, etc., restoration of area to original condition & performing all works as per drawings, specifications and instructions of EIC.
A00601 | Pipeline Warning Signs | No. | 9 | 9232 | 83088
A00602 | Right-of-way Boundary Markers | No. | 6 | 2437 | 14622
A00604 | Direction Markers | No. | 4 | 11171 | 44684
A00700 | Pipeline laying liaisoning with statutory authorities / Permission Issuing Authorities
| Liaisoning with statutory Authority /Permission issuing Authorities for obtaining routine work permit for execution of work and NOC from various Statutory Authority having jurisdiction before/during execution of work and for complying with all stipulations/ conditions and recommendation of the said Authority. Required Permission shall be arranged/obtained by the Owner. (Note :- Payment shall be based on the actual length of pipeline laid). | Mtr. | 950 | 198 | 188100
A00750 | GPRS (Ground Penetration Raddar Survey) in all depth
| Locate Under ground services / utilities within the pipeline route.This shall include identification of under ground utilities by scanning with electromagnetic underground services locator / ground penetrating radar followed by hand excavation to expose the utilities with permission from concerened authorities. laying agency shall prepare a methodology for Scanning and identify the probable areas and obtain prior permission from Engineer-in charge / Client before start of work. Such ground area where utilities are identified by scanning, shall be marked with Red paint. Note: 1.These rates shall be applied only when explicitly permitted by Company. | M2 | 20 | 363 | 7260
A00800 | INSTALLATION OF CARRIER PIPE CROSSINGS BY MOILING METHOD AT CROSSING WITHOUT CASING PIPE
“Complete work of installation of carrier pipe at crossings (between the limits as defined in approved drawings) by moiling method for roads, nallahs, drains and Factory Gates etc., wherever required, in all types of soils, soft rock/ murram. This includes "receiving and taking over" Owner-supplied 3-layer PE coated line pipes from Owner's designated place of issue / dump-site(s) and transportation to Contractor's stock-yard / workshop / work-site including all handling loading, unloading, aligning, etc. supply of all Contractor-supplied materials, manpower, equipment, consumable, other resources and acquiring the required land for storage, fabrication, including string preparation of pipes, welding, welding repair, radiography, coating of field joints with special type Heat Shrink Sleeve and repair of pipeline coating with special repair patch materials as per specification, strapping of HDPE duct as the case may be with main pipeline for laying / blowing of OFC cables, pre-testing, etc. of complete string made for crossing access for Contractor, etc. and execution of, but not limited to, following works in accordance with the specifications and instructions of EIC, and as per all provisions of Contract Document.”
Pre-construction survey based on site-visit, carrying out all additional topographical, hydrological & geo-technical surveys as required for design & construction of crossing, collection of data (if reqd.) from concerned authority including design & detailed engineering and making of crossing drawings for getting their approval from concerned authority / EIC, getting work permit / NOC for crossings as well as utility crossings (if any) encountered during crossings prior to start the execution of work.
Drilling to required depth including maintenance of drill hole in all types of strata (in all types of soils, soft rock/ murram ), all depth to accommodate the pipeline at all conditions encountered during crossing and providing minimum cover specified in code / specification or as decided by concerned authority, whichever is more.
Backfilling of the ditch / trench including restoration and cleanup of area and all other works including cleaning, final hydrotesting, etc. alongwith mainline works (as mentioned in clause no. A00100 above) required as per specification, approved drawings, calculations, methods and to the satisfaction of EIC and / or as directed by concerned authority.
A00801 | Laying of 4" NB Carrier pipe without casing by Moiling method | Mtr. | 15 | 4286 | 64290
Note: i)The length mentioned in SOR is indicative for all the crossing to be done by Moiling & locations shall be decided by GAIL / Consultant prior to start of job depending upon site-condition. ii) Payment for the length of final tied in carrier pipeline string with mainline laid by Moiling are inclusive in this above item rate. No any separate payment shall be made under other clauses mentioned elsewhere.
Note: (1) The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may be increased, decreased or deleted at site at the time of actual execution. Procurement shall be done as per actual site condition, approved construction drawings and as per instruction of EIC. The unit rate shall be operated to work out the final payment to the contractor; (2) In each area, quantities given against individual item may be utilised / used for other consumers in same area.
TOTAL: SECTION-A [MAINLINE WORKS] |  |  |  |  | 4937330

## Sec-B
GAIL (India) Limited | SCHEDULE OF RATES (SOR): SECTION-B [MECHANICAL (PIPING & TERMINAL WORKS)]
Project : Construction of Steel Pipeline and Associated Facilities on CGD Connectivity to M/s Think Gas Macchiwara(Ludhiana)
E-TENDER NO. 8000017675
Currency: INR
SOR Item No. | Description of Item | Unit | Qty. | ESTIMATED UNIT RATE INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT | ESTIMATED TOTAL AMOUNT INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT
|  | (1) | (2) | (3) | (4)
B001000 | PLANT PIPING (ABOVE GROUND)
Complete Carbon Steel Piping Work with painting including all fittings, flanges and supply of all required gaskets, studs bolts & nuts, etc., as described below
Transportation of all piping items from Contractor's storage point to work site complete work of fabrication, erection, painting, testing of pipes, flanges and fittings and making ready for further commissioning / start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, the following works in accordance with relevant specifications indicated in particular job specification & scope of work indicated in SCC, drawings, specification and instructions of EIC and as per all provisions of the Contract Document.
Fabrication including cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, flanges, etc. to match with the matching edges of uneven / different thickness wherever required, welding, attachment of all pipe fittings like elbows, tees, reducers. Supply of nipples, couplings, caps, plugs, gasket, stud bolts, nuts, U-clamps, etc. as required for completion of job.All fittings installation shall be paid linear meter basis under this item only.
Handling and installation of all types & size of valves including assembly of valve accessories/ Actuator, (if any) by bolting, threading or welding, supply and insertion of gaskets, nuts & bolts, nipples, tubing etc. at all elevations of pipe sleepers, supports or overhead on racks, equipments nozzle, skid & painting etc. supply of all consumables, manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of EIC including servicing / cleaning of valve wherever required.
Installation of weldolets, sockolets, flanges, vent and drain point connection, etc., as required.
Erection including prior cleaning, lifting, placing on pipe sleepers and supports, overhead on racks, skids and at all elevations including installation, design & fabrication of all type of supports / jump-over and carrying out connected activities for all types of valves including supply & fixing of gaskets, studs / bolts, nuts wherever required for all sizes, leveling, aligning, joining of flanges, blind flanges, connecting with equipment, nozzles, strainers, tie-in with existing piping / facilities, etc. tapping for inline instruments like pressure gauges, thermowells, sample connection, etc.
Design and Residual Engineering
Preparation of bill of material(BOM)
Preparation of Construction, Fabrication, GAD, isometric and As-built drawings
Carrying out all Non-destructive testing as required except Radiography.
Surface preparation before application of primer by means of sand blasting including supply of approved quality of sand, manpower, machineries, tools & tackles to achieve required roughness as per specification and as per instruction of EIC.
Painting of entire system (including aboveground all pipes fittings, flanges & accessories) suitable for Normal corrosive area environment including supply of approved paints & primers, application of primer & paints, identification lettering / numbering, color-coding, etc. as specified including rub-down & touch-up of shop primer or scrapping of shop primer wherever required by Company and providing scaffolding for all heights, etc.
Cleaning and flushing by water / compressed air, testing of the systems including hydrostatic, pneumatic and any other types of testing as specified, draining, drying by compressed air / other methods approved by Company.
Precommissioning & making operational all piping system and equipments.
Commissioning Contractor scope shall provide all necessary assistance in term of supply of manpower, equipment, tools and tackles required amount of nitrogen for purging of entire terminal piping system including equipments etc. to the company during commissioning activities.
Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start-up.
B001020 | 12" NB Piping different grades & thickness | Mtr. | 5 | 10465 | 52325
B001030 | 8" NB Piping different grades & thickness | Mtr. | 2 | 8440 | 16880
B001050 | 4" NB Piping different grades & thickness | Mtr. | 25 | 6725 | 168125
B001060 | 2" NB Piping different grades & thickness | Mtr. | 12 | 4750 | 57000
B001090 | ¾" NB Piping different grades & thickness | Mtr. | 2 | 1650 | 3300
Note: For Hook-up works at tap-off point, Despatch & Receiving Terminal including making provision for hooking up and carrying out shutdown activities at terminals if necessary shall be paid as per SOR number B008010
B001100 | INSTALLATION OF VALVES
INSTALLATION OF ABOVE GROUND FLANGED VALVES (BALL / PLUG / CHECK / GATE / GLOBE) AS PER DETAILS GIVEN BELOW:
B001130 | Size - 2.0 Inch, Rating - 150#/300#/600# | Nos | 3 | 4350 | 13050
B001200 | INSTALLATION OF ABOVE GROUND BUTT WELDED/SOCKET WELDED VALVES (BALL / PLUG / CHECK / GATE / GLOBE) AS PER DETAILS GIVEN BELOW:
B001210 | Size - 12.0 Inch, Rating - 150#/300#/600# | Nos | 1 | 20310 | 20310
B001230 | Size - 4.0 Inch, Rating - 150#/300#/600# | Nos | 1 | 10155 | 10155
B001240 | Size - 2.0 Inch, Rating -150#/300#/600# | Nos | 4 | 3432 | 13728
B001270 | Size - 3/4 Inch, Rating - 800# | Nos | 3 | 1980 | 5940
B002000 | SUPPLY OF ASSORTED PIPE, VALVES , FITTINGS AND FLANGES
Complete work of supply of pipes, valves, fittings and flanges including all taxes, duties, transportation and inspection charges but not limited to, the following items in accordance with relevant specifications indicated in scope of work , drawings, specification and instructions of EIC and as per all provisions of the Contract Document.
Handling including lifting, transportation from Contractor Stores to Contractor's workshop for fabrication and/ or to work-site for field fabrication and erection for all piping items supplied by Contractor.
B02100 | CARBON STEEL (CS) PIPES
B002107 | CS Pipes 2" NB Sch XS API 5L, Gr.B, Seamless, BE / A 106 Gr.B. | Mtr. | 12 | 1223 | 14676
B002110 | CS Pipes 3/4 " NB Sch 160 , A 106 Gr.B. | Mtr. | 2 | 1007 | 2014
B02200 | VALVES
B02300 | Supply of Socket Welded (SW) Ends Ball Valves as per PMS and Data Sheet
B002310 | Size - 0.75 Inch, 800#, SW Ends, Design Standard - BS EN 1SO 17292, Floating type, Full Bore Ball Valve, Lever Operated | Nos | 3 | 20311 | 60933
B02600 | FLANGES
B02700 | Supply of SW Raised Face (SWRF) Flanges as per details below:
B002740 | Size - 3/4 Inch, 600# , Thk/Sch - 160 , Material - ASTM A105, Face/Finish - RF/125AARH , Dimn. Std. - ASME B16.5 | Nos | 2 | 1305 | 2610
B02800 | Supply of Raised Face Blind Flanges (BLRF) as per details given below:
B002840 | Size - 3/4 Inch, 600# , Material - ASTM A105, Face/Finish - RF/125AARH , Dimn. Std. - ASME B16.5 | Nos | 2 | 465 | 930
B02900 | FITTINGS
B03300 | Supply of Sockolet conforming to MSS-SP-97, Material - ASTM A105 and as per details given below:
B003391 | 4" x 3/4", 6000# | Nos | 2 | 290 | 580
B03400 | Supply of Weldolet conforming to MSS-SP-97, Material - ASTM A105 (CHARPY) and as per details given below:
B003410 | 12" x 2", Thk/Sch - XS | Nos | 2 | 10070 | 20140
B03600 | Supply of Reducer (CONCENTRIC) as per details given below:
B003610 | 2" X 3/4" 6A1 XS x XXS ASTM A 234 GR. WPB B.W, ASME B16.25 | Nos | 1 | 980 | 980
B004000 | RADIOGRAPHY
Performance of radiographic inspection by gamma radiation as per scope of work and as per specifications in piping of all types and thickness including providing / hiring of all necessary equipments, supply of all consumables, and whatever else even though not expressly mentioned but required to perform the work as per specifications and instructions of EIC (full circle re-radiography of the repaired joint and additional radiography necessitated due to poor performance of contractor's welder shall be carried out by the Contractor at his own cost and shall not be paid extra by Company). Radiographs shall be submitted to the EIC for acceptance whose decision shall be final and binding.
B004010 | Radiography 2" NB | Each | 30 | 1393 | 41790
B004020 | Radiography 4" NB | Each | 20 | 1740 | 34800
B004030 | Radiography 8" NB | Each | 2 | 3310 | 6620
B004050 | Radiography 12" NB | Each | 8 | 4965 | 39720
B005000 | HANDLING, LIFTING, TRANSPORTATION (INSTALLATION) OF EQUIPMENTS / VESSELS (Within Campus)
| Handling, including lifting, transportation from Company's stores to Contractor's workshop for fabrication or/and to worksite for field fabrication, assembly of parts / sub-assemblies erection for all vessels, equipments supplied by company aboveground / underground at all elevation / depth, fixing of foundation bolts welding wherever required, aligning, grouting, hooking-up, cleaning and flushing by water draining, drying by compressed air providing all mountings, ancilliary, enabling works as required and completing in all respect as per drawings, specification and instruction of EIC. Contractor's scope shall include supply of all material and accessories including but not limited to any fixtures, clamps, gasket, nut bolts, finish coat of painting including rub-down and touch-up of shop primer / paint scrapping of shop primer / paint and further their painting after application of primer as per specification, wherever required by Company. | Ton | 7 | 9095 | 63665
B006000 | RECEIVING & TAKING OVER, HANDLING, TRANSPORTATION OF PIPES , FLANGES , FITTINGS , VALVES/ FILTERING/ METERING SKIDS/PRS /PIG TRAPS & OTHER EQUIPMENTS ETC (TERMINAL / MAINLINE MATERIAL / SURPLUS MATERIAL) - ANYWHERE IN INDIA
The Contractor shall receive and take over, Handling including lifting, Owner-supplied bare / 3 LPE Coated line pipe / Ball Valves ,Flanges , Fittings, filtering, metering, prs skid, pig traps and any other material from GAIL's designated store, inspection of material at dispatch point as well as destination point and its transportation to work-site (including transit insurance) / return of project surplus / sparable material from Project site / Contractor's store to GAIL's store / warehouse including loading on trucks / trailers, transportation, unloading & stacking on wooden sleepers at Contractor's own stock-yard near work-site(s) / GAIL store (as applicable), including arrangement of truck / trailers / cranes / other material / machinery / manpower / consumables.
B006010 | Transportation by Trailer Fix up to 0-50 KM (Weight up to 20 Ton) per trip | Nos | 1 | 75000 | 75000
B006020 | Transportation by Truck Fix up to 0-50 KM (Weight up to 10 Ton) per trip | Nos | 1 | 45000 | 45000
B006030 | Transportation by Trailer Capacoty 20 Ton (40' L X 8.6' W X 7' H) Beyond 50 KM in addition to SOR Item No. B006010. | Per KM | 1500 | 150 | 225000
B006040 | Transportation by Truck (Weight up to 10 Ton) Beyond 50 KM in addition to SOR Item No. B006020. | Per KM | 1500 | 60 | 90000
Note: (1) Min. 1 TON weightage shall be considered for SOR Item B006040 to process the payment. (2) Unit of measurement MT - Km is product of Weight (in MT) of Material to be transported & road distance (in Kilometers) between dispatch point after 50 Km as shown in the SOR Item No. B006010 & B006020 to destination point. Accordingly, unit rate will be in Rs. / MT-Km; (3) The quantities given in above item no. are tentative only and shall not be considered to be binding. The quantities may be increased, decreased or deleted as per the actual site requirement and instructions / recommendations of Owner. The unit rate shall be operated to work out the final payment to the Contractor; (4) Above price shall be inclusive of all type of taxes & duties, transit insurance during transportation & other insurance, etc. including all financial & commercial implication as per the tender document. No other payment except as per quoted unit rate & executed quantities will be payable by the Owner.
B006030 | Transportation of material for nominal quantities from despatch point to site on "TO PAY BASIS" and legal RTO charges due to the ODC consignments. And payment shall be reimbursed as per SCC Clause no 2.5.7 of Tender Document. Bidder not to quote for this item. | LS |  | Not to be quoted
B007000 | FIRE EXTINGUISHERS (Portable)
Supply, installation and commissioning of the following fire extinguishers:
B007010 | CO2 (10 Kg) considered 1 no. for each locations | No. | 1 | 37600 | 37600
B007020 | 6 kg capacity DCP fire extinguisher (portable) considered 1 no. for each locations | No. | 1 | 20000 | 20000
B007030 | 4 Nos. Sand Buckets with stand & canopy considered 1 set for each location | Set | 2 | 17400 | 34800
B007040 | 75 kg capacity DCP fire extinguisher (portable) considered 1 no. for each locations | No. | 1 | 46000 | 46000
B008000 | Hook-up works at tap-off point, Despatch and Receiving Terminal including making provision for hooking up and carrying out shutdown activities at terminals if necessary (Above Ground)
Carbon Steel Piping Work with painting
Transportation of all piping items from Contractor's storage point to work site complete work of fabrication, erection, painting, testing and making ready for further commissioning / start-up of carbon steel piping of all sizes and ratings including supply of all consumables, equipment, manpower and other resources and execution of, but not limited to, the following works in accordance with relevant specifications indicated in particular job specification & scope of work indicated in SCC, drawings, specification and instructions of EIC and as per all provisions of the Contract Document.
Fabrication including cutting, edge preparation, inclusive of grinding the edges of pipes, fittings, etc. to match with the matching edges of uneven / different thickness wherever required, welding, attachment of all pipe fittings including supply of all consumables required for completion of job.
Supply of all manpower, equipment, etc. for completion of all works as per scope of work and as per drawings, specifications and instructions of EIC wherever required. Preparation of Construction, Fabrication, isometric and As-built drawings.Carrying out Non-destructive testing as required except Radiography.
Surface preparation before application of primer by means of sand blasting including supply of approved quality of sand, manpower, machineries, tools & tackles to achieve required roughness as per specification and as per instruction of EIC.
Testing/ drying/cleaning/Golden Tie -In with existing Pipeline
Precommissioning & making operational all piping system and equipments.
Completion of all such work in all respects as per scope of work and as per drawings, specifications and instructions of the COMPANY and keeping the system ready in all respects for further commissioning and start-up.
B008010 | Piping different grades & thickness | Inch- Dia | 12 | 3480 | 41760
B009000 | INSTALLATION OF FILTERING/ METERING/ PRS SKID AND SCRAPER TRAPS
Installtion of above ground owner supplied Filtering , Metering , PRS Skid, Pig traps and other equipment at work site up to mechanical completition in all respect, inclusive of painting suitable for Normal Corrosive Environment at all elevation , fixing of foundation bolts, welding wherever required, aligning, grouting, hooking-up, enabling works as required and completing in all respect as per drawings, specification and instruction of EIC. Contractor scope also include to provide commissioning assitance during pre-commissing / commissioning of filtering skid/metering skid /PRS/pig trap and other equipments. Note: Instalation and commssioning of Instrumentation items such as Gas Chromatograph (GC) & metering panel(flow computer panel), cable laying are seperately covered under Instrumentation SOR
B009020 | Installation of above ground Filtering/ Metering/ Pressure Reducing Skid up to mechanical completion in all respect inclusive of painting suitable for Normal Corrosive Environment at various loactions. | No | 1 | 263780 | 263780
B0010000 | PIPE SUPPORTS
Supply, fabrication and erection of pipe/ equipment supports (for all sizes/ thickness) including shoes, pipes, cross-ivers, platforms, ladders, railings etc. as required, cradles, turn buckles, T-posts for all types of guides, anchors, special supports for cold/hot insulated pipes etc. if applicable, all necessary equipment, consumables, labour etc. for completing all works including supply of bolts, nuts, washers, U-clamps, wooden blocks etc. as required for supporting, supply and application of paints and primers suitable for normal corrosive painting environment as defined in contract document and as per standard specification for painting specification, Drawings, Specification, Standards, other provisions of Contract and instruction of Engineer-in-Charge.
B0010010 | CS Structural Steel | ton | 0.1 | 141700 | 14170
B0011000 | NITROGEN SUPPLY
B0011010 | Supply of Nitrogen for preservation of Pipeline/ purging of pipeline / hookup & shut down activities . | m3 | 10 | 290 | 2900
Note: (1) The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may be increased, decreased or deleted at site at the time of actual execution. Procurement shall be done as per actual site condition, approved construction drawings and as per instruction of EIC. The unit rate shall be operated to work out the final payment to the Contractor; a (2) Quantities given against individual item may be utilised / used for other consumers in same area.
TOTAL: SECTION-B [MECHANICAL (PIPING & TERMINAL WORKS)] |  |  |  |  | 1546281

## SEC-C
GAIL (India) Limited | SCHEDULE OF RATES (SOR): SECTION-C [CIVIL / STRUCTURAL & ARCHITECTURAL]
Project : Construction of Steel Pipeline and Associated Facilities on CGD Connectivity to M/s Think Gas Macchiwara(Ludhiana)
E-TENDER NO. 8000017675
Currency: INR
Item No. | Description of Item | Unit | Qty. | ESTIMATED UNIT RATE INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT | ESTIMATED TOTAL AMOUNT INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT
|  | (1) | (2) | (3) | (4)
CV003.00.00 | FENCING & GATE
CV003.01.00 | Supplying, fixing and tensioning in position 2.5mm(12gauge), 2 ply, 4 points, GI Barbed wire designation A-1 conforming to IS:278 in horizontal rows and cross diagonals for compound wall "Y" shaped overhang etc. with necessary GI staples, clips and pins, GI straining bolts and binding wire with all labour and materials etc. complete as per drawings, specifications and directions of Engineer-in-Charge.(The barbed wire shall be measured in linear length of the barbed wire actually fixed). | RM | 100 | 285 | 28500
CV003.02.00 | Supplying, fabricating and fixing in position structural steel line posts, straining posts, struts for 'Y' shaped overhang etc. conforming to IS:2062 over brick/stone Masonry/ RCC compound walls/ columns, cutting to required size as per drawings and specifications, welding where necessary, embedding in position, holding to correct level and line, any auxiliary structure for dummy supports, drilling holes and painting as per painting specification attached with tender, cutting brick/rubble/concrete surfaces if necessary, grouting with M20 grade concrete including cost of grout with all labour and material etc. complete as per drawings, specifications and directions of Engineer-in- Charge.( All materials including cement shall be supplied by contractor) For Normal Industrial Environment. | KG | 100 | 244 | 24400
CV003.03.00 | Supplying, fabricating and fixing G.I. chain link fencing with 3.15mm dia. wire, 50x50mm diamond mesh chain link fence fabric conforming to IS:2721 fixed to steel/RCC posts/struts above ground level, including supply of chain link fencing fabric, stretcher bars, staples, etc. required for fixing the fencing, fixing of chain link fencing between straining posts, fixing of bottom of fencing to a concrete sill beams by means of hairpin beams by means of hairpin staples, including supply and fixing line wires, complete as per drawings, specifications and directions of Engineer -in- Charge. | Sqm. | 50 | 2100 | 105000
CV003.04.00 | Providing and fixing in position Steel Entrance Gates consisting of MC- 75 framework for shutters, 20mm square M.S. vertical bars welded to the framework @100mm c/c, 3mm thick M.S. sheet boxing, locking arrangement, 25mm thick, 75mm dia M.S. wheel with ball bearing including fixing the gate to RCC/ masonry by M.S. hinge arrangement (75mm x 75mm x 6mm M.S. angles, bolt, washers) and M.S. hold fast grouted with M-15 grade concrete, providing and fixing M.S. pivot, 50mm x 50mm x 6mm M.S. Tee bent to shape and embedded in road surface for gate opening track, gate stopper, painting the gate with approved shade and quality synthetic enamel paint (two coats) and a coat of approved quality primer, ensuring smooth operation of the gate etc. all complete as per attached standard drawing. | kg | 50 | 238 | 11900
CV009.00.00 | SAND FILLING
CV009.01.00 | Supplying and filling approved SAND of specified quality under floors, in foundations, plinths, tank foundations etc. for all depths and heights including cost of sand,royalties, transportation to site for all leads and lifts,including loading, unloading, spreading in layers of loose thickness not exceeding 150 mm,watering,ramming,compacting with mechanical compactors and/or other equipment to the specified levels to achive 85% relative density as per IS:2720 Part XIV,including preparation of subgrade to the required slope,providing testing apparatus and testing the degree of consolidation all complete as per drawings, specifications and direction of Engineer-in-charge.The rates shall be inclusive of the cost of all labour,material,equipments etc. all complete . | M3 | 15 | 3655 | 54825
CV012.00.00 | EARTH WORK IN FOUNDATION
CV012.01.00 | Earth work in Excavation below ground level for all kinds of works in ALL TYPES OF SOIL as classified in specification for a depth upto 1.5m including removal of vegetation, shrubs and debris, cutting and dressing of sides in slopes, levelling, grading and ramming of bottoms, dewatering of accumulated water from any source and keeping the surface dry for subsequent works and disposal or stacking of excavated material within a lead of 100m, as directed including providing temporary supports to existing service lines like water pipes, sewage pipes, electric overhead and underground cables etc. all complete. | M3 | 100 | 510 | 51000
CV012.02.00 | For depth beyond 1.5m and upto & inclusive of 3.0m. | M3 | 40 | 784 | 31360
CV012.03.00 | Backfilling after execution of the WORK to proper grade and level with selected materials from available excavated soil from spoil heaps, including re-excavating the deposited soil excavated earlier, breaking clods, laying at all depths and heights in layers of thickness not exceeding 15 Cms. watering, rolling and ramming by manual methods/ mechanical compactors to achieve 90% laboratory maximum dry density, dressing, trimming etc. in foundations, plinths, trenches, pits etc. all complete. | M3 | 80 | 350 | 28000
CV012.05.00 | Transporting and disposing the SURPLUS EARTH AND DEBRIS including shrubs and vegetations from construction area beyond the initial lead of 100M including re-excavating the deposited soil excavated earlier, transportation, loading, unloading, laying at all depths and heights, stacking, levelling and dressing both the area (viz. from where the earth is transported and where it is deposited) to required levels and slopes complete with all lifts as directed. For carting on the basis of truck measurements (volume of truck reduced by 30% for voids) i) Upto 1.0Km. | M3 | 60 | 435 | 26100
CV013.00.00 | PLAIN & REINFORCED CEMENT CONCRETE:
CV013.01.00 | Providing and laying PLAIN CEMENT CONCRETE for all depths below and upto plinth level in foundations,drains, fillings, non-suspended floors, pavements & ramps or any other works etc. including shuttering, tamping, ramming, vibrating, curing, shuttering etc. all as specified in any shape, position, thickness and finishing the top surface rough or smooth as specified and directed all complete for concrete of nominal mix 1:4:8 by volume (1 Cement: 4 Coarse Sand: 8 Crushed Stone Aggregates/Gravels with 40mm and down size graded crushed stone aggaregates. | M3 | 20 | 9865 | 197300
CV013.05.00 | Providing and laying REINFORCED CEMENT CONCRETE OF M-25 GRADE with 20mm and down size graded crushed stone aggregates/gravel in SUB-STRUCTURE of all types e.g. foundations, footings, raft, beams, slabs, pile caps, retaining walls, jambs, counterforts, buttresses, trenches, manholes,pipe encasement, catchpits, drains, RCC pits, equipment/machine foundations, pedestals, pipe sleepers, columns, plinth beams, suspended floors, beams, staircases, landings, steps, brackets etc. (including single pour concreting upto 250m3), including cost of admixtures if used,providing pockets, openings, recesses, chamfering etc., wherever required, vibrating, tamping, curing and rendering if required to give a smooth and even surface etc. all complete (excluding the Cost of Reinforcement and Shuttering) for all depths below and upto plinth level in any shape, position and thickness etc. all complete as specified, shown and directed. | M3 | 50 | 13057 | 652850
CV014.00.00 | CENTERING AND SHUTTERING
Providing and fixing CENTERING AND SHUTTERING in foundations, footings, raft beams, slabs, pile caps, retaining walls, jambs, counter-forts, buttresses, trenches, equipment/machine foundations, pedestals, abutments, pipe sleepers, columns, plinth beams, lintels, suspended slabs, beams, staircases, landings, steps, non-circular tunnels/bunkers/silos/ shafts/ hoppers/liquid storage structures etc. including shuttering for single pour concreting, strutting, bracing, propping etc., keeping the same in position during concreting and removal of the same after specified period etc. for Straight/ Inclined Shuttering, keeping necessary provision for inserts, projecting dowels, anchor bolts or any other fixture etc. all complete and as specified and directed.
CV014.01.00 | i) For all depths below and upto & inclusive of plinth level. | M2 | 100 | 696 | 69600
CV015.00.00 | REINFORCEMENT
CV015.01.00 | Supplying and placing in position HIGH STRENGTH DEFORMED STEEL BARS REINFORCEMENT (conforming to IS:1786, Grade Fe 415), for R.C.C. work including transporting the Steel, straightening, cleaning, decoiling, cutting, bending to required shapes and lengths as per details, binding with contractor's own 16 SWG black soft annealed binding wire at every intersection, supplying and placing with proper cover blocks, supports, chairs, overlaps, welding, spacers, fanhooks etc. for all heights and depths etc. all complete as directed. | MT | 3 | 135648 | 406944
CV016.00.00 | STRUCTURAL STEEL WORKS
CV016.01.00 | Supplying, transporting, storing, fabricating in position and testing/examining bolted and/or welded STRUCTURAL STEEL WORKS at all levels and locations including all builtup sections/compound sections made out of rolled sections and/or plates/bent plates in trusses, purlins, wind ties, wind girders, columns, portals, racks, frameworks, crane gantries, surge girders, bracings, floor beams, lifting beams, monorails, platforms, staircases (excluding chequered plates and gratings), ladders, stoppers, brackets, side runners, sagrods, supports for equipment and technological accesories and process piping, hand railings, posts, conveyor galleries, trestles, towers, masts, junction houses etc., cutting to required size, straightening/bending if required, edge preparation, cleaning, preheating, bolting/welding of joints, (including sealing the joints of box sections with continuous welding), finishing edges by grinding, fixing in line and level with temporary staging & bracing and removal of the same after erection, grouting with Ordinary Grout or premix free flow Nonshrink Grout as specified, including preparation and submission of detailed fabrication drawings and applying primer after fabrication as per specification (for normal corrosive environment), etc. all complete | MT | 0.1 | 145080 | 14508
CV017.00.00 | MISCELLANEOUS STEEL WORKS
CV017.02.00 | Supplying, transporting, storing, fabricating and fixing in position M.S. METAL INSERT (with lugs) of any shape made out of flats, plates, rolled sections, pipes etc. providing necessary templates, staging, cutting, straightening, if required, bolting, welding as required and embedding in position on both Plain and Reinforced Cement concrete members inclusive of adjusting shuttering & reinforcement/any other fixture, welding where necessary, tying and holding to correct level, line and position, any auxilliary dummy structures to support the heavy inserts, painting exposed surfaces with a coat of Red Oxide Zinc Chromate Primer etc. all complete for all depths and heights as specified and directed. | MT | 0.1 | 188600 | 18860
CV018.00.00 | BRICK MASONRY
CV018.01.00 | Providing and laying BRICK MASONRY WITH BRICKS OF CLASS 7.5 in cement mortar 1:6 (1 Cement : 6 Sand) in one or more brick thickness and in any shape (excluding circular/curved brick masonry) at all depths and height including the cost of materials, labour, scaffolding/ staging, sampling & testing, soaking of bricks, cutting and laying of bricks, providing recesses, making openings of any shape & size, finishing the joints flush below ground level and raking out the joints above ground level, sealing the gap between masonry and soffit of beam/slab, embedding the fittings & fixtures, curing, etc. all complete as per specifications. | M3 | 1.5 | 11665 | 17497.5
CV018.04.00 | Internal Walls Ordinary plain cement plaster Average 12mm thick 1:4 (1 cement : 4 sand). Cement supplied by the Contractor at their cost | M2 | 10 | 350 | 3500
CV023.04.00 | Supply and installation of Porta Cabin of size (4 mtr X 3 mtr ) as per drawing attached in bid document including associated civil foundation works. | Nos | 1 | 316536 | 316536
| Total amount of quoted prices incusive of all applicable taxex, duties except GST |  |  |  | 2058680.5

## SEC D
GAIL (India) Limited | SCHEDULE OF RATES (SOR): SECTION-D [CATHODIC PROTECTION WORKS]
Project : Construction of Steel Pipeline and Associated Facilities on CGD Connectivity to M/s Think Gas Macchiwara(Ludhiana)
E-TENDER NO. 8000017675
Currency: INR
SOR Item No. | Description of Item | Unit | Qty. | ESTIMATED UNIT RATE INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT | ESTIMATED TOTAL AMOUNT INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT
|  | (1) | (2) | (3) | (4)
D00100 | CATHODIC PROTECTION SYSTEM
All works shall be carried out as per approved drawings and specifications. Work shall include design / residual engineering, preparation of CP schematic drawing, supply, installation, testing and commissioning of complete CP system, all related civil work, including providing foundations, supply of all materials as specified in SCC, instruments, consumables, touch-up epoxy paint as required, including supply of paint, tools, tackles, labor, transportation for satisfactory completion of work and as per directions of EIC. In addition to the items mentioned below the Contractor's scope shall include connecting the new pipelines to existing pipelines/cathode-points of TR units by means of jumpering/bonding.
D00110 | Complete Detailed Survey, Engineering, Supply, laying, installation, termination, testing & commissioning of Cathodic Protection system complete Civil Works and all material and labour as per specifications, drawings and instruction of EIC. Work to be completed in all respects. | KM | 0.95 | 79134 | 75177.3
D00110 | Supply, laying & testing of 600 / 1100V grade single core, stranded tinned copper conductor cables, XLPE insulated / PVC sheathed, armoured as per IS of following sizes. The work shall include excavation for cable trenching at min. 1.2 m below GL in all types of soil including rock, backfilling of cable in trenches, lugging, ferrulling, making termination as per drawings & specification. Supply of all tools, tackles, consumables, etc. for completion of work, in all respect and as per directions of EIC.
D00111 | 35 mm2 | Mtr. | 50 | 765 | 38250
D00112 | 25 mm2 | Mtr. | 20 | 660 | 13200
D00113 | 10 mm2 | Mtr. | 40 | 528 | 21120
D00114 | 6 mm2 | Mtr. | 40 | 528 | 21120
D00120 | Making cable to pipe connections by thermit welding for following cables, including excavation for exposing pipe, removal of coating / wrapping, thermit welding recoating of the area of weld by epoxy filling, holiday testing, backfilling, supply of all tool, tackles, consumables thermit weld kits & labour for satisfactory completion of work.
D00121 | 6 mm2 Cables | No. | 4 | 1320 | 5280
D00122 | 10 mm2 Cables | No. | 4 | 1320 | 5280
D00123 | 25 mm2 Cables | No. | 2 | 2638 | 5276
D00124 | 35 mm2 Cables | No. | 2 | 4025 | 8050
D00130 | Supply & installation of test station as per enclosed drawings and technical specifications. Work shall include all related civil works including foundation, termination of cables inside the test stations along with lugs & ferules sealing of cable entry space with bitumen compound supply of all materials, consumables, tools, tackles, etc. for satisfactory completion of work and as per directions of EIC. | No. | 2 | 50777.65 | 101555.3
D00131 | Supply & installation of Zn anode at a depth of 1.5 - 2.0m on all type of soil including rock alongwith 10m tail cable of 25mm2 high conductivity, tinned, stranded copper conductor, 650 / 1100V grade, XLPE insulated, armoured, PVC sheathed for grounding electrical surges in the pipeline at HT crossings. The work includes excavation, laying of Zn anode of minimum 20 Kg weight, backfilling & all related civil work, complete in all respects. The work shall also include anode to tail cable connection, cable laying and termination inside the test station. | No. | 4 | 37720.54 | 150882.16
D00133 | Supply & installation of Mg anodes after pre-packaged with chemical backfill as per enclosed drawing. The anodes will have to be buried at a depth of 1.5 to 2m on all types of soil including rock at approved location. The work shall include all earth work, laying of anodes & cables in position and termination of cable inside test stations with lugs, shunt & variable resistors, supply of all tools, tackles, consumables, labour transportation of materials, etc. required for satisfactory completion of work and directions of EIC. | No. | 1 | 28980 | 28980
D00134 | Supply, installation, testing and commissioning of spark-gap arrestors across insulating joints. | No. | 2 | 43525 | 87050
Note: (1) The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may be increased, decreased or deleted at site at the time of actual execution. Procurement shall be done as per actual site condition, approved construction drawings and as per instruction of EIC. The unit rate shall be operated to work out the final payment to the contractor; (2) In each area, quantities given against individual item may be utilised / used for other consumers in same area.
D00200 | CATHODIC PROTECTION SYSTEM (PCP)
Design, Engineering, Supply, Installation, Testing & Commissioning of Permanent Cathodic Protection (PCP) System (for 25 years) using LIDA single Electrodes or string (MMO) anodes with backfill, Junction Box, AJB, CJB, Cables, Monitoring System, any equipment and hardwares as per specification including Pre design surveys, Packing, Transportation to Project site, Post Commissioning Surveys of PCP system, system monitoring with other installation items required for completeness of the job. Design package including Site survey, formulae used, Design calculations, BOQ, Technical Specifications and data recording formats, Quality Assurance Control (QA/QC) methodology and submission of monitoring reports for owner evaluation, owner/consultant approved survey report, also includes all materials, equipments, consumables, start up/commissioning spares, etc., including transportation, storage of materials at site, As-built drawings, Documentation and O&M Manual.
D00260 | CIPL Survey | km | 0.95 | 19150 | 18192.5
D00270 | DCVG Survey | km | 0.95 | 20890 | 19845.5
Note: (1) The quantities given above against individual items are indicative and shall not be considered to be binding. The quantities may be increased, decreased or deleted at site at the time of actual execution. Procurement shall be done as per actual site condition, approved construction drawings and as per instruction of EIC. The unit rate shall be operated to work out the final payment to the contractor; (2) In each area, quantities given against individual item may be utilised / used for other consumers in same area.
TOTAL: SECTION-D [CP WORKS] |  |  |  |  | 599258.76

## SEC E
GAIL (India) Limited | SCHEDULE OF RATES (SOR): SECTION-E [ELECTRICAL WORKS]
Project : Construction of Steel Pipeline and Associated Facilities on CGD Connectivity to M/s Think Gas Macchiwara(Ludhiana)
E-TENDER NO. 8000017675
Currency: INR
SOR Item No. | Description of Item | Unit | Qty. | ESTIMATED UNIT RATE INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT | ESTIMATED TOTAL AMOUNT INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT
|  | (1) | (2) | (3) | (4)
E00100 | Supply, installation, testing, commissioning of FLP Street Lighting Fixture suitable for 250W HPMV or Equivalent LED Lamps on Lighting Poles (4mtr Height) with aluminium paint complete with mounting bracket, flameproof control gear box, internal cable from fitting to junction box, flameproof fittings etc. including civil foundation with pipe inserts for cables and connecting work, with all material and labour as per specifications, drawings and instruction of EIC. Work to be completed in all respects. | Nos. | 8 | 39570 | 316560
E01000 | Supply, installation, testing & commissioning of the complete earthing system, earth electrodes/pit, earth main ring, earthing of metering skid, electrical equipments, instrument panels, field instruments, process equipments & pipes / flanges including all associated civil work with all material & labour as per specification & drawings approved by the company. Each earthing system shall include the following.
E01010 | 65mm dia 3 Mtr. Long GI PIPE Electrode with 6mm thick chequered plate cover, display board etc | Nos. | 4 | 20890 | 83560
E01020 | 600x600x3mm copper plate Electrode with 6 mm thick chequered plate cover, display board etc | Nos. | 2 | 24375 | 48750
E01030 | GI Strip (50X6) mm | Mtrs. | 150 | 460 | 69000
E01040 | GI Strip (25X6) mm | Mtrs. | 100 | 330 | 33000
E01050 | 1C 25 Sq.mm PVC insulated Cu Conductor | Mtrs. | 25 | 550 | 13750
E01060 | 10 SWG GI wire | Mtrs. | 125 | 200 | 25000
E01070 | GI Wire, Copper wire, wire rope and all balance earthing material including copper strip (50 mmX 2 mm thick) jumper for flanges etc.as per the specification. | Lot | 1 | 26115 | 26115
E01200 | Supply, laying, installation, termination, testing, commissioning of 1100 Volt PVC insulated, PVC sheathed and armoured / unarmoured cables in trenches, excavated underground / trays, pulling through pipes and its proper sealing including underground trench and supply of hume pipes for road crossing, etc. as required as per specifications and drawings approved by the company.
E01220 | 4C X 6 Sqmm Cu conductor XLPE Insulated Armoured Power Cable of 1100V Grade | Mtrs. | 160 | 725 | 116000
E01230 | 3C X 2.5 Sqmm Cu conductor XLPE Insulated Armoured Power Cable of 1100V Grade | Mtrs. | 75 | 527 | 39525
TOTAL: SECTION-E [ELECTRICAL WORKS] |  |  |  |  | 771260

## SEC F
GAIL (India) Limited | SCHEDULE OF RATES (SOR): SECTION-F [INSTRUMENTATION WORKS]
Project : Construction of Steel Pipeline and Associated Facilities on CGD Connectivity to M/s Think Gas Macchiwara(Ludhiana)
E-TENDER NO. 8000017675
Currency: INR
SOR Item Nos | Description of Item | Unit | Qty. | ESTIMATED UNIT RATE INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT | ESTIMATED TOTAL AMOUNT INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT
|  | (1) | (2) | (3) | (4)
F00100 | Supply, Calibration and Installation of instrumentation items listed below: (For details, refer instrumentation specifications)
F00110 | Pressure Gauge of different Range and rating as per site requirement Supply, testing, installation, erection and commissioning. Also supply of erection material like SS316 tube, SS316 fittings, manifold, mounting stand and all other required material. Bourdon type with 2-way manifold, direct mount, 150mm dial, wetted part SS316, IP 65 rated, blow out protection and shatter proof heavy duty glass. | Nos | 1 | 26115 | 26115
F00130 | Temperature Gauge - skin type, direct mount as per site requirement Supply, testing, installation, erection and commissioning. Also supply of erection material like SS armoured capillary, mounting stand and all other required material. Skin type, direct mount, 150mm dial, wetted part SS316, IP 65 rated and shatter proof heavy duty glass. | Nos | 1 | 19780 | 19780
F00300 | Gas Detection System (GDS) Supply, configuration, testing, installation, erection and commissioning of gas detection system including point gas detectors,control unit and junction boxes. Gas detector control unit shall be installed inside the local control panel. Supply, Laying of cable inside the cable trench, cable tray for hardwired signals and power cables from gas sensors to gas detectors control unit including glanding, termination, ferruling, dressing etc. at both ends. Supply of cable trays, installation and erection of cable trays and, supply of erection materials, cable ferrules, cable lugs, cable tie.
F00310 | IR type, Flame proof, IP-65, housing material SS316 without display, range 0-100% LEL point hydrocarbon gas detector. | Nos | 2 | 23740 | 47480
F00360 | Junction box | Nos | 1 | 50645 | 50645
F00370 | Cables | Mtr | 200 | 633 | 126600
F00500 | Cables, Cables Trays and Junction boxes Supply, laying, installation, erection of signals cable from pressure transmitters, temperature transmitter to junction boxes, junction boxes to local control panel (LCP) and LCP panel to RTU including glanding, termination, ferruling, dressing etc. at both ends. Laying of cable from remote operated valve junction box to local control panel (LCP) and LCP panel to RTU including glanding, termination, ferruling, dressing etc. at both ends. Supply of cable trays, cables glands, junction boxes, erection materials, cable ferrules, cable lugs, cable tie. Installation and erection of cable trays and junction boxes Preparation of cable trench for burying cable, excavation, restoration of trench and compacting. Supply and laying of bricks and sand, pipes at all the crossings etc.
F00580 | Cable Trays (60 mm wide x 30 mm height) | Mtr | 25 | 945 | 23625
F00600 | Metering skid installation, Testing & Commissioning assistance (For instrumentation part ) Installation of telemetry interface panel (TIC) , metering panel(flow computer panel) either in field or in control room, Laying, installation, erection of signals cable from pressure transmitters, temperature transmitter to junction boxes, junction boxes to local control panel (LCP) and LCP panel to RTU including glanding, termination, ferruling, dressing etc. at both ends. Laying of cable from remote operated valve junction box to local control panel (LCP) and LCP panel to RTU including glanding, termination, ferruling, dressing etc. at both ends. Supply of consumables used in cables glanding & junction boxes, erection materials, cable ferrules, cable lugs, cable tie. Preparation of cable trench, excavation, restoration of trench etc. laying of bricks and sand, pipes at all the crossings of cable / tray etc. Providing the resources/manpower for assistance to OEM of metering skid during comissioning of skid. | Nos | 1 | 92325 | 92325
TOTAL: SECTION-F [INSTRUMENTATION WORKS] |  |  |  |  | 386570

## SEC G
GAIL (India) Limited | SCHEDULE OF RATES (SOR): SECTION-G [TELECOM WORKS]
Project : Construction of Steel Pipeline and Associated Facilities on CGD Connectivity to M/s Think Gas Macchiwara(Ludhiana)
E-TENDER NO. 8000017675
Currency: INR
Sl. Nos | Item Nos | Unit | Quantity | ESTIMATED UNIT RATE INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT | ESTIMATED TOTAL AMOUNT INCLUSIVE OF ALL TAXES, DUTIES, LEVIES, FREIGHT, INSURANCE, INCLUDING INSURANCE OF FREE ISSUE MATERIALS, TAXES ON BUILDING AND OTHER CONSTRUCTION WORKERS, ETC. BUT EXCLUDING GST AS DEFINED IN BID DOCUMENT
|  | (1) | (2) | (3) | (4)
G00100 | System design, Inspection & factory testing, FAT, SAT, training, installation, commissioning, Trial run, pre-factory tests, packing, forwarding and supply of all goods including commissioning spares & documentation, pre-commissioning activity for telecom
G00110 | Supply of 24 Fibre Composite armoured Optical Fibre Cable drum (6 fibre G-655 & 18 fibre G-652) of 4 km +/-5% Cable drum length. | Mtr | 950 | 197.835 | 187943.25
G00120 | Supply of jointing closure 24 Fiber, 2 way including all accessories (3M, Siemens, Raychem make only) | Nos | 2 | 26114.22 | 52228.44
G00130 | Supply of 40mm OD permanently lubricated HDPE telecom duct as per technical specifications including manufacturing, factory testing, inspection, packaging, forwarding, transportation, insurance, receipt and storage at site. | Mtr | 950 | 152.988 | 145338.6
Note: In case requirement of 24 Fibre Composite Armoured OFC (SOR item number G00110) is less than 4 kms for any connectivity, GAIL will issue the same as free issue material.
G00200 | Telecommunication Site Work
G00210 | Laying of HDPE Telecom Duct: Laying of 40mm HDPE Ducts in same pipeline trench direct buried or cased crossing through CS / HDPE conduit in all type of soil & terrain, excavated as required, padding, backfilling, etc. including supply of HDPE Duct accessories required including plastic couplers, end plugs, cable sealing plugs, end caps, etc. suitable & sufficient for above supplied ducts, cleaning and sealing of ducts at the end laid drum lengths, preparation and supply of cable blowing pit at each Km jointing of HDPE conduit, testing OD HDPE Duct and accessories after laying preparation of report and final drawing and documents as per specification, joint location marking, erection accessories, as-built, etc. | Mtr | 950 | 73 | 69350
G00220 | Blowing of Optical Fibre Cable inside HDPE Duct: All activities pertaining to Blowing of Optical Fibre Cable in same pipeline trench directly (after testing drum at site), through CS / HDPE conduits along the pipeline also at crossing cable, sealing using all materials required, including laying of warning mats, etc. as per direction of EIC | Mtr | 950 | 80 | 76000
G00240 | Splicing, Jointing of Optical Fiber Cable (Including Supply and Installation of jointing pits including sand, etc. & joint markers) | Nos | 2 | 26115 | 52230
G00250 | Supply of FTC with pig tails other accessories for termination of OFC - 24 Fibre in the Telecom Room | Set | 2 | 26378 | 52756
G00260 | Installation of FTC & Wire mesh, termination of OFC on FTC / DDF inside telecom room, splicing with steet fibre, fibre test, OTDR test, power testing of laid OFC, identification of fault, rectification, earthing, final testing and commissioning, preparation of reports, etc. work complete in all respect with all necessary accessories for all location till final Handing Over and Taking Over by Owner of laid OFC. | Set | 2 | 33514 | 67028
TOTAL: SECTION-G [TELECOM / SCADA WORKS] |  |  |  |  | 702874.29